## Slide 2: Forest Street and First Avenue Drainage Study
Purpose
Preliminary evaluation of existing stormwater collection system
Identify potential solutions to carry forward to design
Study Area
Forest Street
    Between First Avenue and Second Avenue
First Avenue
    Between Forest Street and Butler Street

## Slide 3: Forest Street and First Avenue Drainage Study
Observations
Video dated July 7, 2019 showed flooding at 110 Forest Street
  Inlets were filled with water
  Runoff was not entering inlets - Grate tops are higher than dirt road
As-built plans from December 2017 drainage improvements
  Shows existing road higher than inlets & roadside swales
  Road appears to have eroded in recent years

## Slide 4: Forest Street and First Avenue Drainage Study
Observations
Field Visit on September 23, 2019
  Inlets and French Drain system with perforated pipe
  Standing water in existing inlets about 3’ below grates
    Actual groundwater elevation is higher then original design seasonal high groundwater – Back to back wet seasons
    Poor exfiltration due to siltation and sediment from road

## Slide 5: Forest Street and First Avenue Drainage Study
Drainage Modeling
We modeled the original French Drain system with the following assumptions
  Existing pipes only provided 50% capacity
  Existing French Drains provided no exfiltration
  Simulate 2YR-8HR storm event (3” Rainfall)

## Slide 6: Forest Street and First Avenue Drainage Study
Findings
Flooding is likely due to severe clogging of existing pipes
Possible groundwater infiltration in the French Drains
Estimated runoff could be higher due to impervious area added upstream
Existing ground elevation at R/W contains flooding for 2YR-8HR storm event (3” Rainfall)
Further analysis would be required during design

## Slide 7: Forest Street and First Avenue Drainage Study
Recommendations
Alternative A -
Keep the Existing Dirt Roads
Upsize the existing 15” outfall pipe to 24”

## Slide 8: Forest Street and First Avenue Drainage Study
Recommendations
Improve existing ditches
  Add berm to reduce siltation
  Add articulated ditch blocks
  Add erosion matting to prevent washing out
Add additional ditches at corner of First Ave and Forest Street
Lower inlet elevations or raise elevation of dirt road
Desilt existing system
Create a maintenance plan for road and ditches

## Slide 9: Forest Street and First Avenue Drainage Study
Recommendations
Alternative A - Typical Section

## Slide 10: Forest Street and First Avenue Drainage Study
Recommendations
Alternative B -
Pervious Pavement
Construct pervious pavement along First Ave & Forest Street
Add curb and flume system to tie into existing inlets
Upsize the existing 15” outfall pipe to 24”

## Slide 11: Forest Street and First Avenue Drainage Study
Recommendations
Alternative B - Typical Section

## Slide 12: Forest Street and First Avenue Drainage Study
Other Considerations
The backyards of the homes on Forest Street and First Avenue have a history of flooding
Consider adding additional inlet pipe system with a separate outfall
Would require a drainage easement to construct and maintain system

## Slide 13: Forest Street and First Avenue Drainage Study
Other Considerations